## Sheet1
Addendum | Description | Affected sequences | Affected systems | Summary of changed sequences | Implemented in CDL?
a | Adds Outdoor Air Pollution Mode | 3.1.10; 4.13; 5.1.21; 5.16.4.4; 5.16.5.4; 5.16.6.3; 5.18.7 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units; Single-zone VAV air handling units; Generic sequences or cross-system functions | 3.1.10: New section/content in 2024; no corresponding 2021 section was extracted. 4.13: New section/content in 2024; no corresponding 2021 section was extracted. 5.1.21: New section/content in 2024; no corresponding 2021 section was extracted. 5.16.4.4: replace: 2021 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor air under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] -> 2024 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor airflow under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] ¦ replace: 2021 [When MRA-P is not being calculated for any reason, it shall be set to 100%. 2. Minimum outdoor air control shall be enabled when the unit is in Occupied Mode and either of the following conditions are] -> 2024 [When MRA-P is not being calculated for any reason, it shall be set to 100%. 2. Minimum outdoor airflow control … 5.16.5.4: replace: 2021 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor air control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] -> 2024 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor airflow control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] ¦ replace: 2021 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor air under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] -> 2024 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing … 5.16.6.3: replace: 2021 [5.16.6.3. Minimum Outdoor Air Control Loop a. Minimum outdoor air control loop is enabled when the supply fan is proven ON and] -> 2024 [5.16.6.3. Minimum Outdoor Airflow Control Loop Include the following section if the air handling unit is very large and thus requires staged] ¦ insert: 2021 [5.16.6.3. Minimum Outdoor Air Control Loop a. Minimum outdoor air control loop is enabled when the supply fan is proven ON and the AHU] -> 2024 [5.16.6.3. Minimum Outdoor Airflow Control Loop Include the following section if the air handling unit is very large and thus requires staged outdoor air damper/AFMS assemblies so that airflow measurement can be accurate when the AHU is serving small Zone Groups and/or due to many zones with CO2 DCV or occupancy sensors which can result in very low minimum outdoor air rate setpoints. a. … 5.18.7: insert: 2021 [list (above) and the control logic below. 5.18.7.1. The normal sequencing of the economizer dampers shall be disabled in accordance with Section] -> 2024 [list (above) and the control logic below. 5.18.7.1. The normal sequencing of the economizer dampers shall be disabled if the economizer high limit conditions in Section 5.1.17 are exceeded for 10 minutes or Outdoor Air Pollution Mode is enabled per Section 5.1.16.] ¦ delete: 2021 [(above) and the control logic below. 5.18.7.1. The normal sequencing of the economizer dampers shall be disabled in accordance with Section] -> 2024 [5.18.7.1. The normal sequencing of the economizer dampers shall be disabled if the economizer high limit conditions in Section 5.1.17 are exceeded for 10 minutes or Outdoor Air Pollution Mode is enabled per Section 5.1.16. 5.18.7.2.] ¦ insert: 2021 … | Not assessed (PDF/source comparison only)
b | Revision to the Request-hours calculation to prevent Cumulative%-Request-Hours total from exceeding 100%. | 5.1.14.2 | Generic sequences or cross-system functions | 5.1.14.2: delete: 2021 [5.1.14.2. A “request” is a call to reset a static pressure or temperature setpoint generated by downstream zones or air-handling systems. These requests are sent upstream to the plant or system that serves the zone or air handler that generated the request. a. For each downstream zone or system, and for each type of set-point reset request listed for the zone/system,] -> 2024 [5.1.14.2. For each upstream system or plant setpoint being controlled by a T&R loop, define the following variables. Initial] ¦ replace: 2021 [the plant or system that serves the zone or air handler that generated the request. a. For each downstream zone or system, and for each type of set-point reset request listed for the zone/system, provide the following software] -> 2024 [5.1.14.2. For each upstream system or plant setpoint being controlled by a … | Not assessed (PDF/source comparison only)
c | Addresses an issue with the minimum outdoor airflow setpoint logic for ASHRAE Standard 62.1 ventilation. Relocates the Zpz calculation from the Multiple Zone VAV Air Handling Unit section to the Generic Ventilation Zones section. | 5.2.1.3; 5.16.3.1 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units | 5.2.1.3: replace: 2021 [5.2.1.3. For compliance with the Ventilation Rate Procedure of ASHRAE Standard 62.1-2016, outdoor air and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation] -> 2024 [5.2.1.3. For compliance with the Ventilation Rate Procedure of ASHRAE Standard 62.1, outdoor air and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation] ¦ insert: 2021 [and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. Determine zone air distribution effectiveness Ez. 1. If the DAT at the terminal unit is less than or] -> 2024 [and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. VAV Terminal Units 1. Determine zone air distribution … 5.16.3.1: replace: 2021 [5.16.3.1. Outdoor Airflow Setpoint for ASHRAE Standard 62.1-2016 Ventilation The CO2 DCV strategy for Standard 62.1 currently increases both the zone primary airflow and the population] -> 2024 [5.16.3.1. Outdoor Airflow Setpoint for ASHRAE Standard 62.1 Ventilation The CO2 DCV strategy for Standard 62.1 currently increases both the zone primary airflow and the population] ¦ replace: 2021 [the guideline pending further confirmation of its stability in real-world applications. a. See Section 5.2.1.3 for zone outdoor air requirement Voz. b. See Section 3.1.4.2.a for setpoints DesVou and DesVot. The following logic solves the Standard 62.1 multiple-spaces] -> 2024 [the guideline pending further confirmation of its stability in real-world applications. a. See Section 5.2.1.3 for zone outdoor airflow requirement, Voz. b. See … | Not assessed (PDF/source comparison only)
d | Addresses an issue with heating control for VAV boxes with hot water reheat coils when Vmin* is zero due to no occupancy indicated by the occupancy sensor in occupied-standby mode. | 5.6.4 | VAV terminal units; Hot-water plants; Hydronic distribution systems | 5.6.4: replace: 2021 [minimum Vmin* 0 0 0 0 0 Minimum Vmin* 0 0 0 0 0 Heating minimum Max (Vheat-min, min*) Vheat-min 0 Vheat-max Vheat-max 0 Heating maximum Max (Vheat-max, min*) Vheat-max 0 Vcool-max Vcool-max 0 © ASHRAE. Per] -> 2024 [minimum Vmin* 0 0 0 0 0 Minimum Vmin* 0 0 0 0 0 Heating minimum Max (Vheat-min, Vmin*, Vm) Vheat-min 0 Vheat-max Vheat-max 0 Heating maximum Max (Vheat-max, Vmin*) Vheat-max 0 Vcool-max Vcool-max 0 These sequences use] ¦ replace: 2021 [0 0 0 0 Heating minimum Max (Vheat-min, min*) Vheat-min 0 Vheat-max Vheat-max 0 Heating maximum Max (Vheat-max, min*) Vheat-max 0 Vcool-max Vcool-max 0 © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either] -> 2024 [0 0 0 Heating minimum Max (Vheat-min, Vmin*, Vm) Vheat-min 0 Vheat-max Vheat-max 0 Heating maximum Max … | Not assessed (PDF/source comparison only)
e | Adds zone group mode requests and modifies the conditions required to initiate warm-up, cool-down, setback and setup modes. | 5.3.2.3; 5.3.7; 5.4.6 | Generic sequences or cross-system functions | 5.3.2.3: insert: 2021 [The active setpoints shall be determined by the operating mode of the Zone Group (see Section 5.4.6). a. The set points shall be the occupied set points during occupied mode, warm-up mode, and cooldown mode. b.] -> 2024 [The active setpoints shall be determined by the operating mode of the Zone Group (see Section 5.4.6). a. During Occupied Mode: 1. The cooling set point shall be the occupied cooling set point. 2. The heating set point shall be] ¦ insert: 2021 [active setpoints shall be determined by the operating mode of the Zone Group (see Section 5.4.6). a. The set points shall be the occupied set points during occupied mode, warm-up mode, and cooldown mode. b. The] -> 2024 [determined by the operating mode of the Zone Group (see Section 5.4.6). a. During Occupied Mode: 1. The cooling set point shall be the occupied … 5.3.7: New section/content in 2024; no corresponding 2021 section was extracted. 5.4.6: delete: 2021 [Group’s scheduled occupied start and stop times. b. The schedules have been overridden by the occupant override system. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by IHS Markit under license with ASHRAE - Uncontrolled Copy Licensee=BATTELLE PACIFIC NW DIVISION/5940137102, User=Devaprasad, Karthikeya Not for Resale, 01/27/2022 04:30:51 MST No reproduction or networking permitted without license from IHS Markit --`,,,,```,,,`,`,`,`````,,,``,`-`-`,,`,,`,`,,`--- === PDF page 72 === 70 ASHRAE Guideline 36-2021 Occupant override system is a Web-based system to allow individuals to modify the … | Not assessed (PDF/source comparison only)
g | Addresses an issue with the minimum outdoor airflow control logic for Multiple Zone VAV Air Handling Units with a single common damper for minimum outdoor air and economizer functions with airflow measurement. Default minimum outdoor airflow control loop erroneously set the AHU to 100% outdoor air during Setback, Setup, Warm-up and Cool-down modes. | 5.16.6.3 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units; Economizer systems | 5.16.6.3: replace: 2021 [5.16.6.3. Minimum Outdoor Air Control Loop a. Minimum outdoor air control loop is enabled when the supply fan is proven ON and] -> 2024 [5.16.6.3. Minimum Outdoor Airflow Control Loop Include the following section if the air handling unit is very large and thus requires staged] ¦ insert: 2021 [5.16.6.3. Minimum Outdoor Air Control Loop a. Minimum outdoor air control loop is enabled when the supply fan is proven ON and the AHU] -> 2024 [5.16.6.3. Minimum Outdoor Airflow Control Loop Include the following section if the air handling unit is very large and thus requires staged outdoor air damper/AFMS assemblies so that airflow measurement can be accurate when the AHU is serving small Zone Groups and/or due to many zones with CO2 DCV or occupancy sensors which can result in very low minimum outdoor air rate setpoints. a. … | Not assessed (PDF/source comparison only)
h | Address an issue with the request logic structure, which could cause requests to be generated without its associated loop above 95%. | 5.5.8.1; 5.6.8; 5.7.8; 5.8.8; 5.9.8; 5.10.8; 5.11.8; 5.12.8; 5.13.8; 5.14.8; 5.16.16; 5.17.6; 5.18.15; 5.22.8 | Multiple-zone VAV air handling units; Air handling units; Single-zone VAV air handling units; VAV terminal units; Dual-duct systems; Central plants | 5.5.8.1: insert: 2021 [5.5.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.5.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period] -> 2024 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 … 5.6.8: insert: 2021 [5.6.8. System Requests 5.6.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.6.8. System Requests 5.6.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period] -> 2024 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds … 5.7.8: insert: 2021 [5.7.8. System Requests 5.7.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.7.8. System Requests 5.7.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period] -> 2024 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds … 5.8.8: insert: 2021 [5.8.8. System Requests 5.8.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.8.8. System Requests 5.8.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period] -> 2024 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds … 5.9.8: insert: 2021 [5.9.8. System Requests 5.9.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.9.8. System Requests 5.9.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period] -> 2024 [minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds … 5.10.8: insert: 2021 [5.10.8. System Requests 5.10.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.10.8. System Requests 5.10.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [(5°F) for 2 minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and] -> 2024 [(5°F) for 2 minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. … 5.11.8: insert: 2021 [5.11.8. System Requests 5.11.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F)] -> 2024 [5.11.8. System Requests ThisfileislicensedtoKarthikeyaDevaprasad(karthikeya.devaprasad@pnnl.gov).DownloadDate:1/28/2025 === PDF page 113 === ASHRAE Guideline 36-2024 111 5.11.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature] ¦ insert: 2021 [5.11.8. System Requests 5.11.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [Requests ThisfileislicensedtoKarthikeyaDevaprasad(karthikeya.devaprasad@pnnl.gov).DownloadDate:1/28/2025 === PDF page 113 === ASHRAE Guideline 36-2024 111 5.11.8.1. Cooling SAT Reset Requests a. If the … 5.12.8: insert: 2021 [5.12.8. System Requests 5.12.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.12.8. System Requests 5.12.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [(5°F) for 2 minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and] -> 2024 [(5°F) for 2 minutes and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. … 5.13.8: insert: 2021 [5.13.8. System Requests 5.13.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F)] -> 2024 [5.13.8. System Requests ThisfileislicensedtoKarthikeyaDevaprasad(karthikeya.devaprasad@pnnl.gov).DownloadDate:1/28/2025 === PDF page 121 === ASHRAE Guideline 36-2024 119 5.13.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature] ¦ insert: 2021 [5.13.8. System Requests 5.13.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [Requests ThisfileislicensedtoKarthikeyaDevaprasad(karthikeya.devaprasad@pnnl.gov).DownloadDate:1/28/2025 === PDF page 121 === ASHRAE Guideline 36-2024 119 5.13.8.1. Cooling SAT Reset Requests a. If the … 5.14.8: insert: 2021 [5.14.8. System Requests 5.14.8.1. Cooling SAT Reset Requests a. If the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] -> 2024 [5.14.8. System Requests 5.14.8.1. Cooling SAT Reset Requests a. If the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s cooling setpoint by 3°C (5°F) for 2 minutes and after suppression period] ¦ insert: 2021 [and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the zone temperature exceeds the zone’s cooling setpoint by 2°C (3°F) for 2 minutes and after suppression period due] -> 2024 [and after suppression period due to setpoint change per Section 5.1.20, send 3 requests. b. Else if the Cooling Loop is greater than 95% and the zone temperature exceeds the zone’s … 5.16.16: insert: 2021 [5.16.16. Plant Requests 5.16.16.1. Chilled-Water Reset Requests a. If the supply air temperature exceeds the supply air temperature setpoint by 3°C (5°F) for 2 minutes, send 3] -> 2024 [5.16.16. Plant Requests 5.16.16.1. Chilled-Water Reset Requests a. If the CHW valve position is greater than 95% and the supply air temperature exceeds the supply air temperature setpoint by 3°C (5°F) for 2 minutes, send 3] ¦ insert: 2021 [exceeds the supply air temperature setpoint by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if the supply air temperature exceeds the supply air temperature setpoint by 2°C (3°F) for 2 minutes, send 2] -> 2024 [exceeds the supply air temperature setpoint by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if the CHW valve position is greater than 95% and the supply air temperature exceeds the supply … 5.17.6: insert: 2021 [5.17.6. Plant Requests 5.17.6.1. Hot-Water Reset Requests a. If the supply air temperature is 17°C (30°F) less than setpoint for 5 minutes, send 3 requests. b. Else] -> 2024 [5.17.6. Plant Requests 5.17.6.1. Hot-Water Reset Requests a. If the HW valve position is greater than 95% and the supply air temperature is 17°C (30°F) less than setpoint for 5 minutes, send 3 requests. b. Else] ¦ insert: 2021 [supply air temperature is 17°C (30°F) less than setpoint for 5 minutes, send 3 requests. b. Else if the supply air temperature is 8°C (15°F) less than setpoint for 5 minutes, send 2 requests. c. Else] -> 2024 [supply air temperature is 17°C (30°F) less than setpoint for 5 minutes, send 3 requests. b. Else if the HW valve position is greater than 95% and the supply air temperature is 8°C (15°F) less than setpoint for 5 minutes, … 5.18.15: insert: 2021 [5.18.15. Plant Requests 5.18.15.1. Chilled-Water Reset Requests a. If the supply air temperature exceeds SATsp-C by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if] -> 2024 [5.18.15. Plant Requests 5.18.15.1. Chilled-Water Reset Requests a. If the CHW valve position is greater than 95% and the supply air temperature exceeds SATsp-C by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if] ¦ insert: 2021 [supply air temperature exceeds SATsp-C by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if the supply air temperature exceeds SATsp-C by 2°C (3°F) for 2 minutes, send 2 requests. c. Else if the] -> 2024 [supply air temperature exceeds SATsp-C by 3°C (5°F) for 2 minutes, send 3 requests. b. Else if the CHW valve position is greater than 95% and the supply air temperature exceeds SATsp- C by 2°C (3°F) for 2 minutes, … 5.22.8: insert: 2021 [5.22.8. Plant Requests 5.22.8.1. If There Is a Chilled-Water Coil, Chilled-Water Reset Requests a. All requests shall be suppressed (send 0] -> 2024 [5.22.8. Plant Requests If there is a chilled water coil, keep Sections 5.22.8.1 and 5.22.8.2. Delete otherwise. 5.22.8.1. Chilled-Water Reset Requests a. All requests shall be suppressed (send 0 requests) if fan is not at] ¦ delete: 2021 [5.22.8. Plant Requests 5.22.8.1. If There Is a Chilled-Water Coil, Chilled-Water Reset Requests a. All requests shall be suppressed (send 0 requests) if fan is not at MaxCoolSpeed.] -> 2024 [5.22.8. Plant Requests If there is a chilled water coil, keep Sections 5.22.8.1 and 5.22.8.2. Delete otherwise. 5.22.8.1. Chilled-Water Reset Requests a. All requests shall be suppressed (send 0 requests) if fan is not at MaxCoolSpeed.] ¦ insert: 2021 [is … | Not assessed (PDF/source comparison only)
i | Rearranges the supply fan speed and supply air temperature setpoint sections for Single Zone VAV Air Handling Units to enhance clarify. | 5.18.4.6 | Single-zone VAV air handling units; Air handling units | 5.18.4.6: replace: 2021 [signal: the value of the Heating Loop or Cooling Loop. a. For a heating-loop signal of 100% to 50%, fan speed is reset from MaxHeatSpeed to MinSpeed. b. For a heating-loop signal of 50% to 0%, fan speed] -> 2024 [signal: the value of the Heating Loop or Cooling Loop. a. For a heating-loop signal of 100% to 50% 1. Fan speed is reset from MaxHeatSpeed to MinSpeed. 2. SATsp is Heat_SAT. b. For a heating-loop signal of 50%] ¦ insert: 2021 [Loop. a. For a heating-loop signal of 100% to 50%, fan speed is reset from MaxHeatSpeed to MinSpeed. b. For a heating-loop signal of 50% to 0%, fan speed setpoint is MinSpeed. c. In deadband, fan] -> 2024 [a. For a heating-loop signal of 100% to 50% 1. Fan speed is reset from MaxHeatSpeed to MinSpeed. 2. SATsp is Heat_SAT. b. For a heating-loop signal of 50% to 0% 1. Fan speed setpoint is … | Not assessed (PDF/source comparison only)
j | Separates the ventilation logic for the Single Zone VAV Air Handling Units and VAV terminal units in the generic ventilation zones section. | 5.2.1 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units | 5.2.1: replace: 2021 [5.2.1. Zone Minimum Outdoor Air and Minimum Airflow Setpoints 5.2.1.1. For every zone that requires mechanical ventilation, the zone minimum outdoor airflows and] -> 2024 [5.2.1. Zone Minimum Outdoor Airflow and Minimum Airflow Setpoints 5.2.1.1. For every zone that requires mechanical ventilation, the zone minimum outdoor airflows and] ¦ replace: 2021 [airflows and setpoints shall be calculated depending on the governing standard or code for outdoor air requirements. 5.2.1.2. See Section 3.1.2 for zone minimum airflow setpoint Vmin. The engineer must select between ventilation logic options: If the] -> 2024 [airflows and setpoints shall be calculated depending on the governing standard or code for outdoor air requirements. 5.2.1.2. For VAV terminal units, see Section 3.1.2 for zone minimum airflow setpoint Vmin. The … | Not assessed (PDF/source comparison only)
l | Adds options for control of staged fans and economizer dampers to address large air handling systems. | 3.1.4.2; 4.6; 5.16.1; 5.16.2; 5.16.4; 5.16.6; 5.16.10; 5.16.11; 5.16.14 | Economizer systems; Air handling units; Multiple-zone VAV air handling units; Generic sequences or cross-system functions | 3.1.4.2: replace: 2021 [For projects complying with the Ventilation Rate Procedure of ASHRAE Standard 62.1: 1. DesVou, the uncorrected design outdoor air rate, including diversity where applicable 2. DesVot, design total outdoor air rate (Vou adjusted for ventilation efficiency) DesVou] -> 2024 [For projects complying with the Ventilation Rate Procedure of ASHRAE Standard 62.1: 1. DesVou, the uncorrected design outdoor airflow rate, including diversity where applicable 2. DesVot, design total outdoor airflow rate (Vou adjusted for ventilation efficiency) DesVou] ¦ replace: 2021 [62.1: 1. DesVou, the uncorrected design outdoor air rate, including diversity where applicable 2. DesVot, design total outdoor air rate (Vou adjusted for ventilation efficiency) DesVou and DesVot can be determined using the 62MZCalc spreadsheet provided with] -> 2024 … 4.6: Comparison unavailable from the supplied extraction evidence. 5.16.1: insert: 2021 [fan shall also run when system is in Setback Mode or Warmup Mode (i.e., all modes except unoccupied). Delete the following section if the air-handler serves dual-duct boxes that do not have hot-duct inlet airflow sensors,] -> 2024 [fan shall also run when system is in Setback Mode or Warmup Mode (i.e., all modes except unoccupied). Retain the following if the AHU has multiple supply air fans in an array, each with non-powered backdraft dampers. If VFDs are used, they may each serve multiple fan motors. If ECMs are used, each fan can be controlled individually. But there is little energy value to having more than 6 stages so if there are more than 6 VFDs/ECMs, they should be grouped to be controlled with six digital outputs. c. Staged supply fan controls 1. VFD/ECM groups shall be lead/lag controlled per Section 5.1.15. 2. … 5.16.2: replace: 2021 [Air Temperature Control 5.16.2.1. Control loop is enabled when the supply air fan is proven ON, and disabled and output set to deadband (no heating, minimum economizer) otherwise. 5.16.2.2. Supply Air Temperature Setpoint The default range of] -> 2024 [Air Temperature Control 5.16.2.1. Control loop is enabled when the supply air fan is proven ON, and disabled otherwise. When the loop is disabled, the output shall be set to deadband (no heating, minimum economizer). 5.16.2.2. Supply Air Temperature Setpoint The default range] ¦ insert: 2021 [Control 5.16.2.1. Control loop is enabled when the supply air fan is proven ON, and disabled and output set to deadband (no heating, minimum economizer) otherwise. 5.16.2.2. Supply Air Temperature Setpoint The default range of outdoor] -> 2024 [when the supply air fan is proven ON, and … 5.16.4: replace: 2021 [5.16.4. Minimum Outdoor Air Control with a Separate Minimum Outdoor Air Damper and Differential Pressure Control The engineer must select between ventilation] -> 2024 [5.16.4. Minimum Outdoor Airflow Control with a Separate Minimum Outdoor Air Damper and Differential Pressure Control The engineer must select between ventilation] ¦ replace: 2021 [a. See Section 3.2.1.3.a for design OA DP setpoints. b. See Section 5.16.3.1 for calculation of current outdoor air setpoint MinOAsp. c. The minimum outdoor air DP setpoint MinDPsp shall be calculated as MinDPsp = DesMinDP [MinOAsp Des𝑉𝑜𝑡] -> 2024 [a. See Section 3.2.1.3.a for design OA DP setpoints. b. See Section 5.16.3.1 for calculation of current outdoor airflow setpoint, MinOAsp. c. The minimum outdoor airflow DP setpoint MinDPsp shall be calculated as MinDPsp = DesMinDP … 5.16.6: replace: 2021 [5.16.6. Minimum Outdoor Air Control with a Single Common Damper for Minimum Outdoor Air and Economizer Functions and Airflow Measurement The engineer] -> 2024 [5.16.6. Minimum Outdoor Airflow Control with a Single (or Staged) Common Damper(s) for Minimum Outdoor Airflow and Economizer Functions and Airflow Measurement] ¦ insert: 2021 [5.16.6. Minimum Outdoor Air Control with a Single Common Damper for Minimum Outdoor Air and Economizer Functions and Airflow Measurement The engineer must select between ventilation] -> 2024 [5.16.6. Minimum Outdoor Airflow Control with a Single (or Staged) Common Damper(s) for Minimum Outdoor Airflow and Economizer Functions and Airflow Measurement The engineer must select between ventilation] ¦ replace: 2021 [5.16.6. Minimum Outdoor Air Control with a Single Common Damper for Minimum … 5.16.10: insert: 2021 [5.16.10. Return-Fan Control − Direct Building Pressure 5.16.10.1. See Section 3.1.4.5 for pressure Zone Group assignments. 5.16.10.2. Return fan operates whenever the associated supply fan] -> 2024 [5.16.10. Return-Fan Control − Direct Building Pressure Note that return fan arrays, if used, are not staged (as they are with supply air fans) because there is little energy benefit to doing so and also because staging requires knowledge of return airflow rate and that is not always measured when using Direct Building Pressure control logic. 5.16.10.1. See Section 3.1.4.5 for pressure Zone Group assignments. 5.16.10.2. Return fan operates whenever the associated supply fan] ¦ replace: 2021 [fans for any unit within the pressure zone are proven ON and the minimum outdoor air damper is open. The exhaust dampers shall be closed … 5.16.11: No textual difference detected by normalized extraction; verify formatting and attribution manually. 5.16.14: insert: 2021 [5.16.14. Automatic Fault Detection and Diagnostics The AFDD routines for AHUs continually assess AHU performance by comparing the values of BAS inputs and outputs] -> 2024 [5.16.14. Automatic Fault Detection and Diagnostics Automatic fault detection and diagnostics (AFDD) is a sophisticated system for detecting and diagnosing air- handler faults. To function correctly, AFDD requires specific sensors and data be available, as detailed in the sequences below. If this information is not available, AFDD tests that do not apply should be deleted. The AFDD routines for AHUs continually assess AHU performance by comparing the values of BAS inputs and outputs] ¦ replace: 2021 [any of these components are not present, the associated tests and variables should be omitted from the programming. Note that these alarms rely on reasonably … | Not assessed (PDF/source comparison only)
m | Revision to the leaking valve alarm for all equipment with hot water valves to reduce nuisance alarms. | 5.6.6.5; 5.7.6.6; 5.8.6.6; 5.9.6.6; 5.10.6.6 | VAV terminal units; Hot-water plants; Hydronic distribution systems | 5.6.6.5: insert: 2021 [5.6.6.5. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the] -> 2024 [5.6.6.5. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and] ¦ replace: 2021 [5.6.6.5. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the fan serving the zone is] -> 2024 [5.6.6.5. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and b. DAT is above] ¦ insert: 2021 [5.6.6.5. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the fan serving the zone is proven ON, generate] -> 2024 [5.6.6.5. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 … 5.7.6.6: insert: 2021 [5.7.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the] -> 2024 [5.7.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and] ¦ replace: 2021 [5.7.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the fan serving the zone is] -> 2024 [5.7.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and b. DAT is above] ¦ insert: 2021 [5.7.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, DAT is above AHU SAT by 3°C (5°F), and the fan serving the zone is proven ON, generate] -> 2024 [5.7.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 … 5.8.6.6: insert: 2021 [5.8.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate] -> 2024 [5.8.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and] ¦ replace: 2021 [5.8.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.8.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and b. DAT is above] ¦ insert: 2021 [5.8.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.8.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position … 5.9.6.6: insert: 2021 [5.9.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate] -> 2024 [5.9.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and] ¦ replace: 2021 [5.9.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.9.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and b. DAT is above] ¦ insert: 2021 [5.9.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.9.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position … 5.10.6.6: insert: 2021 [5.10.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate] -> 2024 [5.10.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and] ¦ replace: 2021 [5.10.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.10.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve position is 0%; and b. DAT is above] ¦ insert: 2021 [5.10.6.6. Leaking Valve. If the valve position is 0% for 15 minutes, and DAT is above AHU SAT by 3°C (5°F), generate a Level 4 alarm.] -> 2024 [5.10.6.6. Leaking Valve. If all of the following are true for 15 minutes, generate a Level 4 alarm. a. Valve … | Not assessed (PDF/source comparison only)
n | Addition to allow fans to cycle off during occupied-standby mode for fan-powered terminal units and single zone VAV air handling units. | 5.7.5.5; 5.8.5.1; 5.8.5.2; 5.9.5.5; 5.10.5.5; 5.18.4.1 | Single-zone VAV air handling units; Air handling units; VAV terminal units; Fan-powered terminal units | 5.7.5.5: replace: 2021 [Control a. Fan shall run whenever Zone State is heating. b. If ventilation is according to ASHRAE Standard 62.1-2016, the fan shall run in Deadband and Cooling when the primary air volume is less than Voz for] -> 2024 [Control a. Fan shall run whenever Zone State is heating. b. If ventilation is according to ASHRAE Standard 62.1, in Occupied Mode only, the fan shall run in Deadband and Cooling when both of the following conditions are true for 1] ¦ insert: 2021 [b. If ventilation is according to ASHRAE Standard 62.1-2016, the fan shall run in Deadband and Cooling when the primary air volume is less than Voz for 1 minute and shall shut off when primary air] -> 2024 [according to ASHRAE Standard 62.1, in Occupied Mode only, the fan shall run in Deadband and Cooling when both of the following conditions are true for 1 minute: … 5.8.5.1: delete: 2021 [output shall be mapped to the active airflow setpoint from the minimum endpoint to the cooling maximum endpoint. Discharge Air Temperature Setpoint Heating Loop Signal Cooling Loop Signal Active Primary Airflow Setpoint, Vspt Minimum Cooling Maximum Pfan-htgmax Total CFM (not directly controlled) Pfan-z OA-min Parallel Fan Airflow Setpoint Deadband © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by IHS Markit under license with ASHRAE - Uncontrolled Copy Licensee=BATTELLE PACIFIC NW DIVISION/5940137102, User=Devaprasad, Karthikeya Not for Resale, 01/27/2022 04:30:51 MST No reproduction or … 5.8.5.2: replace: 2021 [shall be the minimum endpoint. b. Heating coil is OFF. c. If ventilation is according to ASHRAE Standard 62.1-2016, parallel fan runs if the active primary airflow setpoint is below Voz. Fan airflow rate setpoint is equal to] -> 2024 [shall be the minimum endpoint. b. Heating coil is OFF. c. If ventilation is according to ASHRAE Standard 62.1, in Occupied Mode only, the fan shall run when both of the following conditions are true for 1 minute: Voz is greater than] ¦ replace: 2021 [minimum endpoint. b. Heating coil is OFF. c. If ventilation is according to ASHRAE Standard 62.1-2016, parallel fan runs if the active primary airflow setpoint is below Voz. Fan airflow rate setpoint is equal to Voz minus the] -> 2024 [coil is OFF. c. If ventilation is according to ASHRAE Standard 62.1, in Occupied Mode only, the fan shall run … 5.9.5.5: replace: 2021 [whenever zone is in heating or cooling Zone State, or if the associated Zone Group is in Occupied Mode. Prior to starting the fan, the damper is first driven fully closed to ensure that the fan is] -> 2024 [whenever zone is in heating or cooling Zone State, or if the associated Zone Group is in Occupied Mode and the active primary airflow setpoint, Vspt, is greater than zero. Prior to starting the fan, the damper is first driven fully closed to ensure that the fan 5.10.5.5: replace: 2021 [whenever zone is in heating or cooling Zone State, or if the associated Zone Group is in Occupied Mode. Prior to starting the fan, the damper is first driven fully closed to ensure that the fan is] -> 2024 [whenever zone is in heating or cooling Zone State, or if the associated Zone Group is in Occupied Mode and the active primary airflow setpoint, Vspt, is greater than zero. Prior to starting the fan, the damper is first driven fully closed to ensure that the fan 5.18.4.1: insert: 2021 [5.18.4.1. The supply fan shall run whenever the unit is in any mode other than Unoccupied Mode.] -> 2024 [5.18.4.1. The supply fan shall run whenever the zone is in heating or cooling Zone State, or if the unit is in Occupied Mode and the minimum outdoor airflow setpoint, MinOAsp, is greater than zero.] ¦ replace: 2021 [5.18.4.1. The supply fan shall run whenever the unit is in any mode other than Unoccupied Mode.] -> 2024 [shall run whenever the zone is in heating or cooling Zone State, or if the unit is in Occupied Mode and the minimum outdoor airflow setpoint, MinOAsp, is greater than zero.] ¦ replace: 2021 [5.18.4.1. The supply fan shall run whenever the unit is in any mode other than Unoccupied Mode.] -> 2024 [or if the unit is in Occupied Mode and the minimum outdoor airflow setpoint, MinOAsp, is greater than | Not assessed (PDF/source comparison only)
o | Addresses a typo, which incorrectly disabled minimum outdoor airflow control when the economizer high limit conditions were exceeded. | 5.16.5.4 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units; Economizer systems | 5.16.5.4: replace: 2021 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor air control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] -> 2024 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor airflow control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] ¦ replace: 2021 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor air under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] -> 2024 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing … | Not assessed (PDF/source comparison only)
p | Addresses errors in the AFDD fault condition equations. Adds option to use airflow monitoring stations for fault conditions that calculate %OA. | 5.16.13.5; 5.16.14 | Multiple-zone VAV air handling units; Air handling units | 5.16.13.5: delete: 2021 [Low building pressure (less than 0 Pa [0.0 in. of water], i.e., negative) for 5 minutes: Level 4. Automatic fault detection and diagnostics (AFDD) is a sophisticated system for detecting and diagnosing air- handler faults. To function correctly, AFDD requires specific sensors and data be available, as detailed in the sequences below. If this information is not available, AFDD tests that do not apply should be deleted.] -> 2024 [Low building pressure (less than 0 Pa [0.0 in. of water], i.e., negative) for 5 minutes: Level 5.16.14: insert: 2021 [5.16.14. Automatic Fault Detection and Diagnostics The AFDD routines for AHUs continually assess AHU performance by comparing the values of BAS inputs and outputs] -> 2024 [5.16.14. Automatic Fault Detection and Diagnostics Automatic fault detection and diagnostics (AFDD) is a sophisticated system for detecting and diagnosing air- handler faults. To function correctly, AFDD requires specific sensors and data be available, as detailed in the sequences below. If this information is not available, AFDD tests that do not apply should be deleted. The AFDD routines for AHUs continually assess AHU performance by comparing the values of BAS inputs and outputs] ¦ replace: 2021 [any of these components are not present, the associated tests and variables should be omitted from the programming. Note that these alarms rely on reasonably … | Not assessed (PDF/source comparison only)
q | Revises demand controlled ventilation calculations to be consistent with ASHRAE Standard 62.1 and California Title 24. | 3.1.1.3; 5.2.1.3; 5.2.1.4; 5.2.3 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units; Generic sequences or cross-system functions | 3.1.1.3: replace: 2021 [3.1.1.3. CO2 Setpoints Space CO2 setpoints are used for demand-controlled ventilation (DCV) and monitoring/alarming as required by LEED and other green] -> 2024 [3.1.1.3. CO2 Maximum Concentration Space CO2 sensors are used for demand-controlled ventilation (DCV) as required by energy standards such as ASHRAE Standard] ¦ replace: 2021 [3.1.1.3. CO2 Setpoints Space CO2 setpoints are used for demand-controlled ventilation (DCV) and monitoring/alarming as required by LEED and other green building standards. It] -> 2024 [3.1.1.3. CO2 Maximum Concentration Space CO2 sensors are used for demand-controlled ventilation (DCV) as required by energy standards such as ASHRAE Standard 90.1 and California] ¦ insert: 2021 [3.1.1.3. CO2 Setpoints Space CO2 setpoints are used for demand-controlled ventilation (DCV) and monitoring/alarming … 5.2.1.3: replace: 2021 [5.2.1.3. For compliance with the Ventilation Rate Procedure of ASHRAE Standard 62.1-2016, outdoor air and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation] -> 2024 [5.2.1.3. For compliance with the Ventilation Rate Procedure of ASHRAE Standard 62.1, outdoor air and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation] ¦ insert: 2021 [and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. Determine zone air distribution effectiveness Ez. 1. If the DAT at the terminal unit is less than or] -> 2024 [and zone minimum setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. VAV Terminal Units 1. Determine zone air distribution … 5.2.1.4: replace: 2021 [5.2.1.4. For compliance with California Title 24, outdoor air setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. Determine the zone] -> 2024 [5.2.1.4. For compliance with California Title 24, outdoor airflow setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. VAV Terminal Units] ¦ insert: 2021 [24, outdoor air setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. Determine the zone minimum outdoor air setpoints Zone-Abs-OA-min and Zone-Des-OA-min. Zone-Abs-OA-min is used in terminal-unit sequences and air-handler] -> 2024 [24, outdoor airflow setpoints shall be calculated as follows: a. See Section 3.1.1.2 for zone ventilation setpoints. b. VAV Terminal Units 1. Determine the zone … 5.2.3: New section/content in 2024; no corresponding 2021 section was extracted. | Not assessed (PDF/source comparison only)
r | Addresses a potential issue where condenser water supply temperature setpoint could get “stuck” if load were to suddenly increase, making it impossible for CWST to achieve setpoint + 0.5°F for hours on end. | 5.20.12.2 | Condenser-water systems; Central plants | 5.20.12.2: replace: 2021 [primarily serving a few large air handlers with similar schedules and plants serving intermittent process loads. Delete otherwise. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by IHS Markit under license with ASHRAE - Uncontrolled Copy Licensee=BATTELLE PACIFIC NW DIVISION/5940137102, User=Devaprasad, Karthikeya Not for Resale, 01/27/2022 04:30:51 MST No reproduction or networking permitted without license from IHS Markit --`,,,,```,,,`,`,`,`````,,,``,`-`-`,,`,,`,`,,`--- === PDF page 214 === 212 ASHRAE Guideline 36-2021 a. Condenser Water Return Temperature (CWRT) Control 1. Tower] -> 2024 … | Not assessed (PDF/source comparison only)
s | Revises the trim and respond resets to direct the designer on how to set the default number of ignored requests for each application, rather than provide a fixed value that will not be appropriate for many applications. | 5.1.14.3; 5.16.1.2; 5.16.2.2; 5.17.1.2; 5.17.2.2; 5.20.5.2; 5.20.5.4; 5.21.4.1 | Multiple-zone VAV air handling units; Air handling units; Dual-duct systems; Condenser-water systems; Central plants; Hot-water plants; Hydronic distribution systems | 5.1.14.3: replace: 2021 [5.1.14.3. For each upstream system or plant setpoint being controlled by a T&R loop, define the following variables. Initial values are defined in system/plant sequences] -> 2024 [5.1.14.3. Trim & Respond logic shall reset the setpoint within the range SPmin to SPmax. When the associated device is OFF, the setpoint shall be SP0.] ¦ replace: 2021 [5.1.14.3. For each upstream system or plant setpoint being controlled by a T&R loop, define the following variables. Initial values are defined in system/plant sequences below. Values for trim, respond, time step, etc.] -> 2024 [5.1.14.3. Trim & Respond logic shall reset the setpoint within the range SPmin to SPmax. When the associated device is OFF, the setpoint shall be SP0. The reset] ¦ replace: 2021 [5.1.14.3. For each upstream system or plant setpoint being controlled by a … 5.16.1.2: delete: 2021 [setpoint. Setpoint shall be reset using T&R logic (see Section 5.1.14) using the parameters shown in Table 5.16.1.2. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by IHS Markit under license with ASHRAE - Uncontrolled Copy Licensee=BATTELLE PACIFIC NW DIVISION/5940137102, User=Devaprasad, Karthikeya Not for Resale, 01/27/2022 04:30:51 MST No reproduction or networking permitted without license from IHS Markit --`,,,,```,,,`,`,`,`````,,,``, === PDF page 112 === 110 ASHRAE Guideline 36-2021 Table 5.16.1.2 Trim & Respond Variables Variable Value Device Supply fan SP0 120 Pa (0.5 in. of water)] -> … 5.16.2.2: insert: 2021 [as in a VAV dual-fan dual-duct system, or the climate severely limits the number of available economizer hours. If using this logic, the engineer should oversize interior zones and rooms with high cooling loads (design them] -> 2024 [as in a VAV dual-fan dual-duct system, or the climate severely limits the number of available economizer hours. This lower range also can be used to indirectly limit zone humidity in humid climates, e.g. setting both Max_ClgSAT and OAT_Max to 16°C (60°F) ensures that supply air dew point temperature is always below 16°C (60°F), effectively maintaining space dew point temperature below that limit in zones with low latent loads such as offices. See Section 5.16.2.3 for other more direct ways to limit zone humidity. If using this logic, the engineer should oversize interior zones and rooms with … 5.17.1.2: delete: 2021 [Table 5.17.1.2 are suggested as a starting place; they will most likely require adjustment during the commissioning/tuning phase. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by IHS Markit under license with ASHRAE - Uncontrolled Copy Licensee=BATTELLE PACIFIC NW DIVISION/5940137102, User=Devaprasad, Karthikeya Not for Resale, 01/27/2022 04:30:51 MST No reproduction or networking permitted without license from IHS Markit --`,,,,```,,,`,`,`,`````,,,``,`-`-`,,`,,`,`,,`--- === PDF page 147 === ASHRAE Guideline 36-2021 145 Table 5.17.1.2 Trim & Respond Variables Variable Value Device Supply fan … 5.17.2.2: replace: 2021 [5.17.2.2. Supply Air Temperature Setpoint a. During Occupied Mode (Table 5.17.2.2). Setpoint shall be reset using T&R logic (see Section 5.1.14) between 21°C (70°F) and Max_HtgSAT. See Section 3.1.5.1 for] -> 2024 [5.17.2.2. Supply Air Temperature Setpoint a. During Occupied Mode, setpoint shall be reset using T&R logic (see Section 5.1.14) between 21°C (70°F) and Max_HtgSAT. See Section 3.1.5.1 for] ¦ delete: 2021 [Table 5.17.2.2 are suggested as a starting place; they will most likely require adjustment during the commissioning/tuning phase. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission. Copyright American Society of Heating, Refrigerating and Air-Conditioning Engine Provided by … 5.20.5.2: insert: 2021 [on the current value of the logic variable called “CHW Plant Reset” as shown below and described subsequently. The recommended logic first resets differential pressure setpoint to maximum before resetting chilled water supply temperature setpoint down] -> 2024 [on the current value of the logic variable called “CHW Plant Reset” as shown below and described subsequently. ThisfileislicensedtoKarthikeyaDevaprasad(karthikeya.devaprasad@pnnl.gov).DownloadDate:1/28/2025 === PDF page 218 === 216 ASHRAE Guideline 36-2024 The recommended logic first resets differential pressure setpoint to maximum before resetting chilled water supply temperature setpoint down] ¦ replace: 2021 [variety of climate zones during the development of ASHRAE’s “Fundamentals of Design and Control of Central Chilled-Water Plants” Self- Directed Learning … 5.20.5.4: replace: 2021 [Pumped Loops: Chilled water supply temperature setpoint, CHWSTsp, shall be reset using Trim & Respond logic with the following parameters: Variable Value Device Any CHW Pump SP0 CHWSTmin SPmin CHWSTmin SPmax 60°F Td 15 minutes T 5 minutes] -> 2024 [Pumped Loops: Chilled water supply temperature setpoint, CHWSTsp, shall be reset using Trim & Respond logic with the parameters shown in Table 5.20.5.4: Table 5.20.5.4 Trim & Respond Variables Variable Value Device Any CHW Pump SP0 CHWSTmin SPmin CHWSTmin SPmax 15.6°C (60°F) Td 15 minutes T 5] ¦ replace: 2021 [& Respond logic with the following parameters: Variable Value Device Any CHW Pump SP0 CHWSTmin SPmin CHWSTmin SPmax 60°F Td 15 minutes T 5 minutes I 2 R Cooling CHWST Reset Requests SPtrim +0.75°F SPres -1°F SPres-max] -> 2024 [5.20.5.4: Table 5.20.5.4 Trim & Respond … 5.21.4.1: replace: 2021 [5.21.4.1. Plant hot water supply temperature setpoint shall be reset using Trim & Respond logic with the following parameters: Variable Value Device Any HW Pump Distribution Loop © ASHRAE. Per international copyright law, additional reproduction, distribution, or] -> 2024 [5.21.4.1. Plant hot water supply temperature setpoint shall be reset using Trim & Respond logic with the parameters shown in Table 5.21.4.1: Table 5.21.4.1 Trim & Respond Variables Variable Value Device Any HW Pump Distribution Loop SP0 SPmax SPmin 32.2°C (90ºF) for condensing and hybrid boiler] ¦ delete: 2021 [reset using Trim & Respond logic with the following parameters: Variable Value Device Any HW Pump Distribution Loop © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form … | Not assessed (PDF/source comparison only)
t | Revises the location of where requests are defined to recognize that they are used more broadly than indicated by their current definition as a subsection of Trim and Respond Setpoint Requests. | 5.1.14; 5.1.16 | Generic sequences or cross-system functions | 5.1.14: replace: 2021 [reduces the setpoint at a fixed rate until a downstream zone is no longer satisfied and generates a request. When a sufficient number of requests are present, the setpoint is increased in response. The importance of each] -> 2024 [reduces the setpoint at a fixed rate until a downstream zone is no longer satisfied and generates a “request”, as defined in Section 5.1.16. When a sufficient number of requests are present, the setpoint is increased in response. The importance of each] ¦ replace: 2021 [It typically does generate low-frequency cyclic hunting, but this behavior is slow enough to be nondisruptive. See Section 5.1.14.4 for an example of T&R implementation. 5.1.14.1. T&R set-point reset logic and zone/system reset requests, where referenced in] -> 2024 [It typically does generate low-frequency cyclic hunting, but … 5.1.16: replace: 2021 [5.1.16. Not Used This section was deleted in Addendum a. To avoid section numbering changes, an empty section was inserted.] -> 2024 [5.1.16. Requests 5.1.16.1. A “request” is a call to reset a setpoint or enable equipment to run that is generated by downstream zones or air-handling systems. These requests are sent upstream to the plant or system that serves the zone or air handler that generated the request. a. For each downstream zone or system, and for each type of request listed for the zone/system, provide the following software points: 1. Importance-Multiplier (default = 1) Importance-Multiplier is used to scale the number of requests the zone/system is generating. A value of zero causes the requests from that zone or system to be ignored. A value greater than one can be used to effectively increase the number of … | Not assessed (PDF/source comparison only)
u | Updates all fan and pump alarms to be consistent throughout. | 5.7.6.3; 5.8.6.3; 5.9.6.3; 5.10.6; 5.16.13.2; 5.17.3.2; 5.18.12.2; 5.19.2.2; 5.22.5.2 | Multiple-zone VAV air handling units; Air handling units; Single-zone VAV air handling units; VAV terminal units; Dual-duct systems; Chilled-water plants; Central plants | 5.7.6.3: replace: 2021 [5.7.6.3. Fan alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded on, status off: Level 2 b. Commanded off,] -> 2024 [5.7.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the equipment has] ¦ replace: 2021 [alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded on, status off: Level 2 b. Commanded off, status on: Level 4] -> 2024 [5.7.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm … 5.8.6.3: replace: 2021 [5.8.6.3. Fan alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded ON, status OFF Level 2 b. Commanded OFF,] -> 2024 [5.8.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the equipment has] ¦ replace: 2021 [alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded ON, status OFF Level 2 b. Commanded OFF, status ON: Level 4] -> 2024 [5.8.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until … 5.9.6.3: replace: 2021 [5.9.6.3. Fan alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded ON, status OFF: Level 2 b. Commanded OFF,] -> 2024 [5.9.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the equipment has] ¦ replace: 2021 [alarm is indicated by the status input being different from the output command after a period of 15 seconds after a change in output status. a. Commanded ON, status OFF: Level 2 b. Commanded OFF, status ON: Level 4 © ASHRAE. Per international] -> 2024 [5.9.6.3. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do … 5.10.6: replace: 2021 [than zero, generate a Level 3 alarm. c. If a zone has an Importance-Multiplier of 0 (see Section 5.1.14.2.a.1 for its static pressure reset T&R control loop, low airflow alarms shall be suppressed for that zone. 5.10.6.2.] -> 2024 [than zero, generate a Level 3 alarm. c. If a zone has an Importance-Multiplier of 0 (see Section 5.1.16) for its static pressure reset T&R control loop, low airflow alarms shall be suppressed for that zone. 5.10.6.2.] ¦ insert: 2021 [ON, and the DAT is 17°C (30°F) less than setpoint for 10 minutes, generate a Level 3 alarm. c. If a zone has an Importance-Multiplier of 0 (see Section 5.1.14.2.a.1) for its hot-water reset T&R control] -> 2024 [ON, and the DAT is 17°C (30°F) less than setpoint for 10 minutes, generate a Level 3 alarm. … 5.16.13.2: insert: 2021 [5.16.13.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2] -> 2024 [5.16.13.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not] ¦ insert: 2021 [5.16.13.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2 b. Commanded off, status] -> 2024 [5.16.13.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the] ¦ delete: 2021 [5.16.13.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, … 5.17.3.2: insert: 2021 [5.17.3.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, status OFF: Level 2] -> 2024 [5.17.3.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not] ¦ insert: 2021 [5.17.3.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, status OFF: Level 2 b. Commanded OFF, status] -> 2024 [5.17.3.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the] ¦ delete: 2021 [5.17.3.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, … 5.18.12.2: insert: 2021 [5.18.12.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, status OFF: Level 2] -> 2024 [5.18.12.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not] ¦ insert: 2021 [5.18.12.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, status OFF: Level 2 b. Commanded OFF, status] -> 2024 [5.18.12.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the] ¦ delete: 2021 [5.18.12.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded ON, … 5.19.2.2: insert: 2021 [5.19.2.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2] -> 2024 [5.19.2.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not] ¦ insert: 2021 [5.19.2.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2 b. Commanded off, status] -> 2024 [5.19.2.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the] ¦ delete: 2021 [5.19.2.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, … 5.22.5.2: insert: 2021 [5.22.5.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2] -> 2024 [5.22.5.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not] ¦ insert: 2021 [5.22.5.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, status off: Level 2 b. Commanded off, status] -> 2024 [5.22.5.2. Fan alarm is indicated by the status input being different from the output command for 15 seconds. a. Commanded on, status off: Level 2. Do not evaluate the alarm until the] ¦ delete: 2021 [5.22.5.2. Fan alarm is indicated by the status being different from the command for a period of 15 seconds. a. Commanded on, … | Not assessed (PDF/source comparison only)
v | Adds a way to establish different demand limit adjustments to different space types. | 3.1.1.1; 5.3.2.6; 5.3.2.7 | Generic sequences or cross-system functions | 3.1.1.1: insert: 2021 [(AHU) equipment schedules. They can also be generically listed by zone type, such as the example in (a) below. a. Default setpoints shall be based on zone type as shown in Table 3.1.1.1. Table 3.1.1.1 Default] -> 2024 [(AHU) equipment schedules. They can also be generically listed by zone type, such as the example in (a) and (b) below. a. Default setpoints shall be based on zone type as shown in Table 3.1.1.1-1. Table 3.1.1.1-1 Default] ¦ replace: 2021 [the example in (a) below. a. Default setpoints shall be based on zone type as shown in Table 3.1.1.1. Table 3.1.1.1 Default Setpoints Zone Type Occupied Unoccupied Heating Cooling Heating Cooling VAV 21°C (70°F) 24°C (75°F) 16°C] -> 2024 [in (a) and (b) below. a. Default setpoints shall be based on zone type as shown in Table 3.1.1.1-1. Table 3.1.1.1-1 Default Setpoints Zone … 5.3.2.6: replace: 2021 [user interface. Changes due to demand limits are not cumulative. a. At demand-limit Level 1, increase setpoint by 0.5°C (1°F). b. At demand-limit Level 2, increase setpoint by 1°C (2°F). c. At demand-limit Level 3, increase setpoint by] -> 2024 [user interface. Changes due to demand limits are not cumulative. a. At demand-limit Level 1, increase setpoint by offset listed in Section 3.1.1.1.b. b. At demand-limit Level 2, increase setpoint by offset listed in Section 3.1.1.1.b. c. At demand-limit Level 3,] ¦ replace: 2021 [a. At demand-limit Level 1, increase setpoint by 0.5°C (1°F). b. At demand-limit Level 2, increase setpoint by 1°C (2°F). c. At demand-limit Level 3, increase setpoint by 2°C (4°F).] -> 2024 [Level 1, increase setpoint by offset listed in Section 3.1.1.1.b. b. At demand-limit Level 2, increase setpoint by … 5.3.2.7: replace: 2021 [user interface. Changes due to demand limits are not cumulative. a. At demand-limit Level 1, decrease setpoint by 0.5°C (1°F). b. At demand-limit Level 2, decrease setpoint by 1°C (2°F). c. At demand-limit Level 3, decrease setpoint by] -> 2024 [user interface. Changes due to demand limits are not cumulative. a. At demand-limit Level 1, decrease setpoint by offset listed in Section 3.1.1.1.b. b. At demand-limit Level 2, decrease setpoint by offset listed in Section 3.1.1.1.b. c. At demand-limit Level 3,] ¦ replace: 2021 [a. At demand-limit Level 1, decrease setpoint by 0.5°C (1°F). b. At demand-limit Level 2, decrease setpoint by 1°C (2°F). c. At demand-limit Level 3, decrease setpoint by 2°C (4°F). Heating demand limits may be desirable in buildings] -> 2024 [Level 1, decrease setpoint by offset listed in Section … | Not assessed (PDF/source comparison only)
w | Removes the need to update list of all parameters and setpoints referenced in each section. | 5.5.3; 5.6.3; 5.7.3; 5.8.3; 5.9.3; 5.10.3; 5.11.3; 5.12.3; 5.13.3; 5.14.3; 5.18.2; 5.18.3; 5.19.2.3; 5.20.1; 5.21.1; 5.22.2; 5.22.3 | Single-zone VAV air handling units; Air handling units; VAV terminal units; Condenser-water systems; Central plants; Chilled-water plants; Hot-water plants; Hydronic distribution systems | 5.5.3: replace: 2021 [5.5.3. See Section 3.1.2.1 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and zone maximum heating airflow] -> 2024 [5.5.3. See Sections 3.1.1 and 3.1.2.1 for operating parameters and setpoints. If the minimum ventilation rate is more than 25% or so of] ¦ replace: 2021 [5.5.3. See Section 3.1.2.1 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and zone maximum heating airflow setpoint Vheat-max. If the minimum ventilation rate is more than 25% or so] -> 2024 [5.5.3. See Sections 3.1.1 and 3.1.2.1 for operating parameters and setpoints. If the minimum ventilation rate is more than 25% or so of the cooling maximum, or] ¦ replace: 2021 [5.5.3. See Section 3.1.2.1 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint … 5.6.3: replace: 2021 [5.6.3. See Section 3.1.2.2 for zone minimum airflow setpoints Vmin, zone maximum cooling airflow setpoint Vcool-max, zone maximum heating airflow setpoint] -> 2024 [5.6.3. See Sections 3.1.1 and 3.1.2.2 for operating parameters and setpoints.] ¦ replace: 2021 [5.6.3. See Section 3.1.2.2 for zone minimum airflow setpoints Vmin, zone maximum cooling airflow setpoint Vcool-max, zone maximum heating airflow setpoint Vheat-max, zone minimum heating airflow setpoint Vheat-min, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.6.3. See Sections 3.1.1 and 3.1.2.2 for operating parameters and setpoints.] ¦ replace: 2021 [maximum cooling airflow setpoint Vcool-max, zone maximum heating airflow setpoint Vheat-max, zone minimum heating airflow setpoint Vheat-min, and the maximum DAT rise above heating setpoint MaxT.] … 5.7.3: replace: 2021 [5.7.3. See Section 3.1.2.3 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise] -> 2024 [5.7.3. See Sections 3.1.1 and 3.1.2.3 for operating parameters and setpoints.] ¦ replace: 2021 [5.7.3. See Section 3.1.2.3 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.7.3. See Sections 3.1.1 and 3.1.2.3 for operating parameters and setpoints.] ¦ replace: 2021 [5.7.3. See Section 3.1.2.3 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.7.3. See Sections 3.1.1 and 3.1.2.3 for operating parameters and 5.8.3: replace: 2021 [5.8.3. See Section 3.1.2.4 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, the parallel fan maximum heating] -> 2024 [5.8.3. See Sections 3.1.1 and 3.1.2.4 for operating parameters and setpoints. 5.8.3.1. Pfan-z is the lowest rate at which the fan will operate] ¦ replace: 2021 [5.8.3. See Section 3.1.2.4 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, the parallel fan maximum heating airflow setpoint Pfan-htgmax, and the maximum DAT rise above heating setpoint MaxT. 5.8.3.1. Pfan-z is the lowest rate at which the] -> 2024 [5.8.3. See Sections 3.1.1 and 3.1.2.4 for operating parameters and setpoints. 5.8.3.1. Pfan-z is the lowest rate at which the fan will operate when it is turned] ¦ replace: 2021 [airflow setpoint Vmin, zone maximum cooling … 5.9.3: replace: 2021 [5.9.3. See Section 3.1.2.5 for zone minimum airflow setpoints Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise] -> 2024 [5.9.3. See Sections 3.1.1 and 3.1.2.5 for operating parameters and setpoints.] ¦ replace: 2021 [5.9.3. See Section 3.1.2.5 for zone minimum airflow setpoints Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.9.3. See Sections 3.1.1 and 3.1.2.5 for operating parameters and setpoints.] ¦ replace: 2021 [5.9.3. See Section 3.1.2.5 for zone minimum airflow setpoints Vmin, zone maximum cooling airflow setpoint Vcool-max, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.9.3. See Sections 3.1.1 and 3.1.2.5 for operating parameters and 5.10.3: replace: 2021 [5.10.3. See Section 3.1.2.6 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, the series fan maximum heating] -> 2024 [5.10.3. See Sections 3.1.1 and 3.1.2.6 for operating parameters and setpoints.] ¦ replace: 2021 [5.10.3. See Section 3.1.2.6 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, the series fan maximum heating airflow Sfan-htgmax, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.10.3. See Sections 3.1.1 and 3.1.2.6 for operating parameters and setpoints.] ¦ replace: 2021 [minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, the series fan maximum heating airflow Sfan-htgmax, and the maximum DAT rise above heating setpoint MaxT.] -> 2024 [5.10.3. See Sections 3.1.1 and 3.1.2.6 for … 5.11.3: replace: 2021 [5.11.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow] -> 2024 [5.11.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.11.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.11.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.11.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.11.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and 5.12.3: replace: 2021 [5.12.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating] -> 2024 [5.12.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.12.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.12.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.12.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.12.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and 5.13.3: replace: 2021 [5.13.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating] -> 2024 [5.13.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.13.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.13.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.13.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.13.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and 5.14.3: replace: 2021 [5.14.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating] -> 2024 [5.14.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.14.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.14.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and setpoints.] ¦ replace: 2021 [5.14.3. See Section 3.1.2.7 for zone minimum airflow setpoint Vmin, zone maximum cooling airflow setpoint Vcool-max, and the zone maximum heating airflow setpoint Vheat-max.] -> 2024 [5.14.3. See Sections 3.1.1 and 3.1.2.7 for operating parameters and 5.18.2: replace: 2021 [5.18.2. See Section 3.1.6.1 for Cool_SAT, Heat_SAT, and MaxDPT.] -> 2024 [5.18.2. See Sections 3.1.1 and 3.2.2 for operating parameters and setpoints.] ¦ replace: 2021 [5.18.2. See Section 3.1.6.1 for Cool_SAT, Heat_SAT, and MaxDPT.] -> 2024 [5.18.2. See Sections 3.1.1 and 3.2.2 for operating parameters and setpoints.] ¦ replace: 2021 [5.18.2. See Section 3.1.6.1 for Cool_SAT, Heat_SAT, and MaxDPT.] -> 2024 [5.18.2. See Sections 3.1.1 and 3.2.2 for operating parameters and 5.18.3: replace: 2021 [5.18.3. See Section 3.2.2 for MinSpeed, MaxHeatSpeed, MaxCoolSpeed, MinPosMin, MinPosMax, DesPosMin, DesPosMax, MinRelief, MaxRelief, and S-R-DIFF.] -> 2024 [5.18.3. Not 5.19.2.3: New section/content in 2024; no corresponding 2021 section was extracted. 5.20.1: replace: 2021 [5.20.1. See Section 3.1.7 for CHWSTminX, CWRTdesX, CWSTdesX, CH-LOT, CHW-MinFlowX, CHW- DesFlowX, LIFTminX, LIFTmaxX, QchX, PCHWFdesign, SCHWFdesign, MinUnloadCapX, DAHX, DTWB, DACT,] -> 2024 [5.20.1. See Sections 3.1.7 and 3.2.3 for operating parameters and setpoints.] ¦ delete: 2021 [5.20.1. See Section 3.1.7 for CHWSTminX, CWRTdesX, CWSTdesX, CH-LOT, CHW-MinFlowX, CHW- DesFlowX, LIFTminX, LIFTmaxX, QchX, PCHWFdesign, SCHWFdesign, MinUnloadCapX, DAHX, DTWB, DACT, HXFdesign, and HXDP-Design. See Section 3.2.3 for CHW-DPmax, LocalCHW-DPmax, Cw- DesPumpSpdStage, MinCWVlvPos, MinCWPspeed, HxPumpDesSpd, Ch-MaxPriPumpSpdStage, and CH-MinPriPumpSpdStage.] -> 2024 [5.20.1. See Sections 3.1.7 and 3.2.3 for operating parameters and setpoints.] ¦ delete: 2021 [CHWSTminX, CWRTdesX, CWSTdesX, CH-LOT, CHW-MinFlowX, CHW- DesFlowX, … 5.21.1: replace: 2021 [5.21.1. See Section 3.1.8 for HWSTmax, HW-LOT, HW-MinFlowX, HW-DesFlowX, QbX, B-FiringMinX, PHWFdesign, and SHWFdesign. See Section 3.2.4 for HW-DPmax, LocalHW-DPmax, and] -> 2024 [5.21.1. See Sections 3.1.8 and 3.2.4 for operating parameters and setpoints.] ¦ delete: 2021 [5.21.1. See Section 3.1.8 for HWSTmax, HW-LOT, HW-MinFlowX, HW-DesFlowX, QbX, B-FiringMinX, PHWFdesign, and SHWFdesign. See Section 3.2.4 for HW-DPmax, LocalHW-DPmax, and B- MinPriPumpSpdStage.] -> 2024 [5.21.1. See Sections 3.1.8 and 3.2.4 for operating parameters and setpoints.] ¦ delete: 2021 [5.21.1. See Section 3.1.8 for HWSTmax, HW-LOT, HW-MinFlowX, HW-DesFlowX, QbX, B-FiringMinX, PHWFdesign, and SHWFdesign. See Section 3.2.4 for HW-DPmax, LocalHW-DPmax, and B- MinPriPumpSpdStage.] -> 2024 [5.21.1. See Sections 3.1.8 and 3.2.4 for operating … 5.22.2: replace: 2021 [5.22.2. See Section 3.1.7 for Cool_SAT, Heat_SAT, and DP100. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in] -> 2024 [5.22.2. See Sections 3.1.7 and 3.2.3 for operating parameters and setpoints.] ¦ insert: 2021 [5.22.2. See Section 3.1.7 for Cool_SAT, Heat_SAT, and DP100. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either] -> 2024 [5.22.2. See Sections 3.1.7 and 3.2.3 for operating parameters and setpoints.] ¦ replace: 2021 [5.22.2. See Section 3.1.7 for Cool_SAT, Heat_SAT, and DP100. © ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital] -> 2024 [5.22.2. See Sections 3.1.7 and 3.2.3 for operating parameters and setpoints.] ¦ replace: 2021 … 5.22.3: replace: 2021 [5.22.3. See Section 3.2.3 for MinSpeed, DeadbandSpeed, MaxHeatSpeed, and MaxCoolSpeed.] -> 2024 [5.22.3. Not | Not assessed (PDF/source comparison only)
y | Fixes an error the MZVAV AHUs with separate minimum outdoor air dampers which could cause both the outside air and return air damper to close when the supply air temperature control loop is wound up and minimum outdoor airflow control is enabled. | 5.16.4.4; 5.16.5.4 | Ventilation systems; Air handling units; Multiple-zone VAV air handling units | 5.16.4.4: replace: 2021 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor air under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] -> 2024 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor airflow under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] ¦ replace: 2021 [When MRA-P is not being calculated for any reason, it shall be set to 100%. 2. Minimum outdoor air control shall be enabled when the unit is in Occupied Mode and either of the following conditions are] -> 2024 [When MRA-P is not being calculated for any reason, it shall be set to 100%. 2. Minimum outdoor airflow control … 5.16.5.4: replace: 2021 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor air control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] -> 2024 [(a). Delete this flag note after selections have been made. a. For units with return fans Minimum outdoor airflow control is enabled when return damper position exceeds MRA-P because it cannot be assumed that the combination of] ¦ replace: 2021 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing sufficient outdoor air under these conditions. The 20% threshold can be increased to ensure minimum outdoor airflow will be maintained but] -> 2024 [be assumed that the combination of the minimum and the economizer outdoor air dampers are providing … | Not assessed (PDF/source comparison only)
z | Adds options for humidity limiting logic. | 3.1.1.4; 3.1.4.6; 4.1; 4.2; 4.3; 4.4; 4.5; 4.6; 5.3.6.2; 5.5.8.3; 5.6.8.5; 5.7.8.5; 5.8.8.5; 5.9.8.5; 5.10.8.5; 5.11.8.6; 5.12.8.6; 5.13.8.6; 5.14.8.6; 5.16.2.2; 5.16.2.3 | Humidity-control systems; Air handling units; Multiple-zone VAV air handling units; VAV terminal units; Generic sequences or cross-system functions | 3.1.1.4: New section/content in 2024; no corresponding 2021 section was extracted. 3.1.4.6: New section/content in 2024; no corresponding 2021 section was extracted. 4.1: Comparison unavailable from the supplied extraction evidence. 4.2: Comparison unavailable from the supplied extraction evidence. 4.3: Comparison unavailable from the supplied extraction evidence. 4.4: Comparison unavailable from the supplied extraction evidence. 4.5: Comparison unavailable from the supplied extraction evidence. 4.6: Comparison unavailable from the supplied extraction evidence. 5.3.6.2: New section/content in 2024; no corresponding 2021 section was extracted. 5.5.8.3: New section/content in 2024; no corresponding 2021 section was extracted. 5.6.8.5: New section/content in 2024; no corresponding 2021 section was extracted. 5.7.8.5: New section/content in 2024; no corresponding 2021 section was extracted. 5.8.8.5: New section/content in 2024; no corresponding 2021 section was extracted. 5.9.8.5: New section/content in 2024; no corresponding 2021 section was extracted. 5.10.8.5: New section/content in 2024; no corresponding 2021 section was extracted. 5.11.8.6: New section/content in 2024; no corresponding 2021 section was extracted. 5.12.8.6: New section/content in 2024; no corresponding 2021 section was extracted. 5.13.8.6: New section/content in 2024; no corresponding 2021 section was extracted. 5.14.8.6: New section/content in 2024; no corresponding 2021 section was extracted. 5.16.2.2: insert: 2021 [as in a VAV dual-fan dual-duct system, or the climate severely limits the number of available economizer hours. If using this logic, the engineer should oversize interior zones and rooms with high cooling loads (design them] -> 2024 [as in a VAV dual-fan dual-duct system, or the climate severely limits the number of available economizer hours. This lower range also can be used to indirectly limit zone humidity in humid climates, e.g. setting both Max_ClgSAT and OAT_Max to 16°C (60°F) ensures that supply air dew point temperature is always below 16°C (60°F), effectively maintaining space dew point temperature below that limit in zones with low latent loads such as offices. See Section 5.16.2.3 for other more direct ways to limit zone humidity. If using this logic, the engineer should oversize interior zones and rooms with … 5.16.2.3: replace: 2021 [5.16.2.3. Supply air temperature shall be controlled to setpoint using a control loop whose output is mapped to sequence the heating coil] -> 2024 [5.16.2.3. Supply Air Temperature Setpoint Limit for Humidity Control a. The Humidity_SAT_Limit shall be the lowest value dictated by the following strategies: Note that control based on outdoor air dew] ¦ replace: 2021 [5.16.2.3. Supply air temperature shall be controlled to setpoint using a control loop whose output is mapped to sequence the heating coil (if applicable), outdoor air damper, return air] -> 2024 [5.16.2.3. Supply Air Temperature Setpoint Limit for Humidity Control a. The Humidity_SAT_Limit shall be the lowest value dictated by the following strategies: Note that control based on outdoor air dew point will prevent the introduction of large volumes of humid … | Not assessed (PDF/source comparison only)